## Slide 1: BRE: urbaneer findings
Robbie Thompson BRE 15 July 2016

## Slide 2: Three tower blocks
Block 1
1967-1975 build, uninsulated cavity wall, double glazed with electric storage heaters.
Block 2
1950-1966 concrete system build, single glazed with underfloor electric heating, no thermostatic or time control
Block 3
1967-1975 concrete system build, double glazed, electric storage heaters

## Slide 3: Three tower blocks
Block 1
External wall insulation Double glazing District heating
Block 2
External wall insulation Double glazing District heating
Block 3
Enerphit (passivhaus) retrofit External Wall Insulation MVHR Double Glazing Enclosed Walkways Not Complete

## Slide 4: Property overview
Building | Properties
Enfield | 10
Portsmouth | 10
Nottingham | 13
Data collection
1* Electricity
3* T&RH
3* PIR Occupancy
1* CO2
Occupancy assessment
EPC, Green Deal

## Slide 5: First Winter data analysis – Internal Temperature
Chart: Block 3 Temperature
| 41974 | 42005 | 42036 | 42064 | 42095 | 42125 | 42156 | 42186 | 42217 | 42248
Measured Internal Temperature | 18.7208 | 18.3535 | 17.5091 | 18.1384 | 18.8625 | 19.4222 | 21.2458 | 22.0434 | 21.8024 | 19.2951
RdSAP assumed temperature | 19.39 | 19.39 | 19.42 | 19.43 | 19.44 | 19.45 | 19.45 | 19.43 | 19.42 | 19.4 | 19.39 | 19.38
External Temperature | 5.1333 | 4.8387 | 3.8571 | 6.5484 | 8.9 | 11.0968 | 13.8 | 15.129 | 15.3548 | 12.0667 | 12 | 0
Chart: Block 2 Temperature
| 41974 | 42005 | 42036 | 42064
Pre Insulation Internal Temperature | 15.5794 | 15.1031 | 16.2308 | 17.3671
Post Insulation Internal Temperature | 19.5326 | 20.1699 | 22.7259 | 24.232 | 24.032 | 22.7467
RdSAP Assumed Internal Temperature | 20.05 | 20.04 | 20.05 | 20.05 | 20.07 | 20.08 | 20.09 | 20.09 | 20.09 | 20.08
External Temperature | 4.9355 | 4.4194 | 3.7143 | 6.2903 | 9.1667 | 10.6774 | 14.2333 | 16.0968 | 16.5484 | 12.3 | 12.5
Chart: Block 1 Temperature
| 41974 | 42005 | 42036 | 42064 | 42095 | 42125 | 42156 | 42186 | 42217 | 42248
Measured Internal Temperature | 22.8148 | 23.0493 | 22.9129 | 23.6522 | 24.2327 | 24.2862 | 24.7957 | 24.9631 | 24.0873 | 24.1562
RdSAP assumed temperature | 17.83 | 17.78 | 17.9 | 18.17 | 18.48 | 18.88 | 19.16 | 19.29 | 19.29 | 19.09
External Temperature | 7.0645 | 5.9677 | 5.5357 | 8.1935 | 11 | 13.3548 | 16.8667 | 19.0645 | 18.5806 | 14.4667
Block 1 and 3
External temp coupling
Low winter temps (below CIBSE Comfort)
High summer temp
No property meets RdSAP assumptions
Block 2
Constant high temperatures

## Slide 6: Heat Maps
Block 3
Ineffective storage heaters
Block 1
Consistently low temperatures
Block 2
All day high temperatures

## Slide 7: First Winter data analysis
 | Heat Loss Parameter W/m²K | Heat Loss Parameter W/m²K RdSAP | Data Quality Score
P1 | 2.23 | 2.32 | 60%
P2 | 2.15 | 2.32 | 81%
P3 | 1.53 | 1.55 | 46%
P4 | 1.50 | 1.55 | 61%
P5 | 2.58 | 3.00 | 75%
Mean | 2.00 |  | RdSAP: 2.15
Standard Deviation | 0.47 |  | 
 | Heat Loss Parameter W/m²K | Data Quality Score
N1 | 1.58 | 40%
Mean | 1.58 | RdSAP: 2.92
Standard Deviation | N/A | 

## Slide 8: First Winter data analysis - Electricity use
Chart: Block 2 Electricity Use
| 42034 | 42063 | 42093
Measured, Pre Insulation | 31.589 | 28.642 | 23.7327
Measured Post Insulation | 18.0121 | 10.0572 | 3.5252 | 5.8017 | 6.7447
RdSAP Pre Insulation | 51.8936 | 51.3133 | 43.1409
RdSAP Post Insulation | 22.0237 | 18.0211 | 11.9703 | 11.743 | 11.9796
Chart: Block 3 Electricity Use
| 42003 | 42034 | 42063 | 42093 | 42124 | 42154 | 42185 | 42215 | 42246 | 42277
Actual Electricity Use | 41.4176 | 44.3711 | 44.2499 | 35.9684 | 19.7481 | 18.0319 | 11.6277 | 12.0294 | 8.7955
RdSAP Electricity Use | 62.2094 | 60.6089 | 58.4603 | 47.0933 | 33.4347 | 20.9182 | 12.7918 | 12.4957 | 12.8291
Below predicted energy use, likely to lead to poor returns from insulation

## Slide 9: First Winter data analysis - Occupancy
Chart: Time of Day
| 0 | 4.1666666666666664E-2 | 8.3333333333333329E-2 | 0.125 | 0.16666666666666666 | 0.20833333333333334 | 0.25 | 0.29166666666666669 | 0.33333333333333331 | 0.375 | 0.41666666666666669 | 0.45833333333333331 | 0.5 | 0.54166666666666663 | 0.58333333333333337 | 0.625 | 0.66666666666666663 | 0.70833333333333337 | 0.75 | 0.79166666666666663 | 0.83333333333333337 | 0.875 | 0.91666666666666663 | 0.95833333333333337
Weekdays | 0.73184 | 0.7367 | 0.66506 | 0.71215 | 0.76975 | 0.70961 | 0.62263 | 0.52394 | 0.50874 | 0.5163 | 0.38109 | 0.41109 | 0.44379 | 0.42005 | 0.53138 | 0.48348 | 0.50868 | 0.45436 | 0.53553 | 0.59587 | 0.65762 | 0.64949 | 0.65787 | 0.64349
Weekends | 0.67118 | 0.73921 | 0.73009 | 0.76268 | 0.73578 | 0.65781 | 0.59227 | 0.48524 | 0.53579 | 0.55158 | 0.4345 | 0.50777 | 0.4988 | 0.49942 | 0.55365 | 0.53575 | 0.49997 | 0.53268 | 0.58149 | 0.61369 | 0.67992 | 0.69946 | 0.69863 | 0.73399
High occupancy – doesn’t equate to high energy use

## Slide 10: Second Winter data Analysis Internal Temperatures - Block 1
Chart: Block 1: pre and post retrofit
| Dec | Jan | Feb | Mar
Before-retrofit average temperature | 17.4156 | 16.1955 | 17.4897 | 18.169
After-retrofit average temperature | 21.1785 | 20.9909 | 21.4695 | 21.077
Before-retrofit external temperature | 4.9 | 4.4 | 3.6 | 6.3
After-retrofit external temperature | 9.5 | 5.4 | 4.8 | 5.5
Chart: Pre-retrofit Would you generally describe the temperature in your home as…
| Uncomfortably cold | Comfortably cool | Comfortable | Comfortably warm | Uncomfortably warm
B1. Would you generally describe the temperature in your home as… | 1 | 2 | 0 | 0 | 0
Chart: Post-retrofit Would you generally describe the temperature in your home as…….
| Uncomfortably cold | Comfortably cool | Comfortable | Comfortably warm | Uncomfortably warm
Would you generally describe the temperature in your home as……. | 0 | 0 | 6 | 1 | 0
Consistently higher internal temperatures within CIBSE Comfort Criteria
Better Occupancy feedback
Minimal overheating

## Slide 11: Second Winter data Analysis Internal Temperatures - Block 2
Similar temperatures
Better occupancy feedback
Minimal overheating
Chart: Monthly average temperaute [°C]
| Dec | Jan | Feb | Mar
Before-retrofit average temperature | 21.4904 | 22.0994 | 22.3921 | 22.6708
After-retrofit average temperature | 22.5681 | 22.2009 | 21.1436 | 21.7472
Before-retrofit external temperature | 4.9 | 4.4 | 3.6 | 6.3
After-retrofit external temperature | 10.8 | 6 | 6 | 7.2
Chart: Pre-retrofit Would you generally describe the temperature in your home as…
| Uncomfortably cold | Comfortably cool | Comfortable | Comfortably warm | Uncomfortably warm
B1. Would you generally describe the temperature in your home as… | 4 | 1 | 0 | 4 | 0
Chart: Pre-retrofit Would you generally describe the temperature in your home as...
| Uncomfortably cold | Comfortably cool | Comfortable | Comfortably warm | Uncomfortably hot
Would you generally describe the temperature in your home as: | 0 | 1 | 0 | 2 | 0

## Slide 12: CO2 Levels – Block 1
Ref | 14 | 13 | 12 | 11 | 10 | 6 | 5 | 3 | 2 | Average
Max Value (ppm) | 1,830 | 3,050 | 1,480 | 1,730 | 3,430 | 3,750 | 2,730 | 2,000 | 2,920 | 2,640
> 1,000ppm | 12.3% | 47.9% | 1.5% | 29.0% | 49.0% | 32.9% | 41.1% | 20.1% | 46.6% | 33.5%
> 1,500ppm | 2.0% | 17.7% | 0.0% | 1.5% | 21.9% | 11.4% | 14.1% | 1.5% | 19.9% | 11.0%
> 2,000ppm | 0.0% | 3.3% | 0.0% | 0.0% | 7.9% | 3.5% | 3.5% | 0.0% | 5.0% | 2.9%
Ref | 13 | 11 | 10 | 6 | 3 | 2 | Average
Max Value (ppm) | 2540 | 2460 | 2510 | 2540 | 1150 | 2540 | 2,290
> 1,000ppm | 46.6% | 8.5% | 7.2% | 9.8% | 2.4% | 31.5% | 17.7%
> 1,500ppm | 6.4% | 0.6% | 0.4% | 1.3% | 0.0% | 5.2% | 2.3%
> 2,000ppm | 0.4% | 0.0% | 0.2% | 0.2% | 0.0% | 0.3% | 0.2%
Pre Retrofit CO2
Post Retrofit CO2
Post retrofit shows better maximum CO2 levels
Poor CO2 can impact concentration, headaches and drowsiness
May indicate regular window opening – lower energy savings

## Slide 13: CO2 Levels – Block 2
Pre Retrofit CO2
Post Retrofit CO2
Post retrofit shows similar CO2 levels and high
Two properties had CO2 levels close to HSE’s workplace exposure limit of >5,000 for more than 8 hours
CO2 levels highest 5am suggesting living used as bedroom
Ref | 10 | 5 | 3 | Average
Maximum CO2 ppm | 1,430 | 1,130 | 6,970 | 3,180
> 1,000ppm | 1.6% | 0.13% | 51.1% | 17.6%
> 1,500ppm | 0.0% | 0.0% | 22.0% | 7.3%
> 2,000ppm | 0.0% | 0.0% | 10.9% | 3.6%
Ref | 10 | 9 | 7 | 5 | 4 | 2 | Average
Maximum CO2 ppm | 1,640 | 6,430 | 1,290 | 1,210 | 1,760 | 2,210 | 2,420
> 1,000ppm | 3.4% | 70.7% | 0.6% | 0.3% | 8.7% | 7.4% | 15.2%
> 1,500ppm | 0.1% | 40.7% | 0.0% | 0.0% | 0.68% | 0.2% | 6.9%
> 2,000ppm | 0.0% | 26.8% | 0.0% | 0.0% | 0.0% | 0.2% | 4.5%

## Slide 14: Humidity - Block 1
Percentage of hours where average hourly humidity exceeded 70%
Percentage of hours where average hourly humidity below 40%
CIBSE Guide A recommends that relative-humidity should be in the range of 40-70%.
High humidity within the property has dropped significantly.
Humidity drop is likely to lead to a significant improvement in condensation risk, mould growth and high humidity associated health issues.
Low humidity has increased.
 | N12 | N11 | N10 | N9 | N8 | N7 | N5 | N4 | N3 | N2 | N1 | Average
Before Retrofit | 1.0% | 7.8% | 4.1% | 0.2% | 7.3% | 13.5% | 6.8% | 8.0% | 82.9% | 23.0% | 15.4% | 15.5%
After Retrofit | NA | 8.7% | NA | 0.2% | 0.0% | 0.1% | NA | 0.0% | 0.6% | 0.0% | 0.2% | 1.2%
 | N12 | N11 | N10 | N9 | N8 | N7 | N5 | N4 | N3 | N2 | N1 | Average
Before Retrofit | 9.7% | 10.5% | 0.7% | 2.1% | 0.0% | 0.2% | 5.2% | 0.0% | 0.0% | 0.0% | 0.0% | 2.6%
After Retrofit | NA | 3.3% | NA | 15.6% | 5.5% | 5.5% | NA | 6.6% | 0.0% | 21.7% | 26.7% | 10.6%

## Slide 15: Humidity - Block 2
 | E9 | E8 | E7 | E6 | E5 | E4 | E3 | E2 | Average
Before Retrofit | 19.5% | 0.0% | 0.0% | 1.5% | 0.0% | 0.0% | 0.0% | 3.5% | 3.0%
After Retrofit | 2.0% | NA | 0.0% | 0.5% | 0.0% | 0.0% | NA | NA | 0.5%
 | E9 | E8 | E7 | E6 | E5 | E4 | E3 | E2 | Average
Before Retrofit | 8.0% | 81.9% | 85.6% | 30.3% | 53.9% | 36.0% | 32.1% | 3.3% | 41.4%
After Retrofit | 48.3% | NA | 88.8% | 5.8% | 33.8% | 44.1% | NA | NA | 44.2%
Percentage of hours where average hourly humidity exceeded 70%
Percentage of hours where average hourly humidity below 40%
CIBSE Guide A recommends that relative-humidity should be in the range of 40-70%.
Humidity within the property is almost unchanged but often below 40%

## Slide 16: Mould risk
Chart: Block 1 Pre-retrofit Have you noticed any mould on the walls/ceiling?
| Yes | No | Don’t know
c6. Have you noticed any mould on the walls/ceiling? | 2 | 1 | 0
Chart: Block 2 before-retrofit Have you noticed any mould on the walls/ceilings?
| Yes | No | Don’t know
c6. Have you noticed any mould on the walls/ceiling? | 4 | 6 | 0
Chart: Block 2 post-retrofit Last winter did you notice any mould on the walls or ceilings?
| Yes | No | Don't know
Last winter did you notice any mould on the walls or ceilings | 1 | 2 | 0
Chart: Block 1 after-retrofit Last winter did you notice any mould on the walls or ceilings?
| Yes | No | Don't know
Last winter did you notice any mould on the walls or ceilings | 1 | 6 | 0
Mould risk dramatically reduced
Only mould in flat above unheated space
Mould risk reduced
Only mould in flat above unheated space (with high internal temperatures)

## Slide 17: Energy use – Block 2
 | Floors | Pre RdSAP cost per flat (mid) | Post RdSAP cost per flat (mid) | Cost per flat (Pre) | Cost per flat (Post) | Saving per flat | Percentage saving
Meter 1 | G,1,2,3 | £884 | £423 | £1,150 | £1,070 | £80 | 7.0%
Meter 2 | 4,5,6 | £884 | £423 | £1,200 | £700 | £530 | 43.0%
Meter 3 | 7,8,9 | £884 | £423 | £1,400 | £1,040 | £380 | 26.4%
Meter 4 | 10,11,12 | £884 | £423 | £1,000 | £920 | £120 | 11.7%
Average |  | £884 | £423 | £1,260 | £970 | £280 | 21.8%
Total building |  | £44,500 | £21,150 | £60,300 | £46,500 | £13,800 | 21.8%
Energy saving 22%
Pre retrofit - 34% worse than RdSAP
Post retrofit – 134% worse than RdSAP
Partly due to high internal temperatures
Likely to be due to open windows.
Chart: Monthly CO2 Variation
| 41974 | 42005 | 42036 | 42064 | 42064 | 42095 | 42125 | 42156 | 42186 | 42217 | 42248 | 42309 | 42339 | 42370 | 42401 | 42430
E10 | 539.1983 | 560.79 | 598.5178 | 653.4418 | 653.4418 | 663.8903 | 671.811 | 709.2547 | 669.43 | 711.5056 | 646.8867 | 616.2237 | 690.5492 | 687.4568 | 665.2652 | 605.3503
E9 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 870.7145 | 887.3703 | 765.3999 | 717.4173 | 1075.5688 | 1539.8787 | 1418.4706 | 1850.026 | 1674.9139 | 1665.3582
E8 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 493.1196 | 502.1872 | #N/A | #N/A | #N/A | #N/A
E7 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 469.9192 | 491.3506 | 473.2086 | 530.4197 | 533.8803 | 471.7704
E5 | 482.4472 | 508.8643 | 533.6367 | 459.0817 | 459.0817 | 480.0501 | 450.7264 | 465.1491 | 483.1569 | 527.0713 | 540.8481 | 582.5315 | 512.2887 | 526.9726 | 540.2677 | 537.9983
E4 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 521.5552 | 480.7686 | 518.5039 | 536.8865 | 584.8246 | 718.6876 | 586.2968 | 656.1665 | 701.7726 | 627.1376
E3 | #N/A | 992.5784 | 1063.5309 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
E3 | 2196.8317 | 1098.4521 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
E2 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 618.57 | 703.3911 | 721.0979 | 649.1961 | #N/A | 689.6476

## Slide 18: Retrofit summary
Block 1:
  More comfortable,
  Better air quality
  Low mould risk
Block 2:
  Minimal to internal temperature, energy bills or air quality change
  Savings not materialised due to poor heating system